## Battery Calculations
Project
Completed by |  |  |  | Date | 2019-09-03 | [5 empty] | Device Programming Points Summary
MX4 pro supports Maximum of 942 device points
Select Nittan evo+ Panel |  | Quiescent Load |  |  | Fire Alarm Load |  |  | Q | A |  | MX5 Pro supports a maximum of 1000 device points
5100 | I(A) | X | Total | I(A) | X | Total | OFF | 0.072 | 0.125 | 4 | Total of device points |  | 0
Chassis | 0.072 | 1 | 0.072 | 0.125 | 1 | 0.125 | DIM | 0.082 | 0.125 | 24 |  | Loop | Total | Max Loop | Cable | Qty
Sensor / Loop Current* | 0 | 1.25 | 0 | 0.04 | 1.25 | 0.05 | ON | 0.102 | 0.125 | 48 | Circuit | Status | Volt Drop | Length(M) | Type | Devices
Loop Driver Loop 1 | 0.042 | 1 | 0.042 | 0.042 | 1 | 0.042 |  |  |  | 72 | Loop 1 | Loop ok | 0.968 | 2000 | FP200 1.5mm | 0
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | MXP-503 | 0.02 | 0.02
Loop Driver Loop 2 | 0 | 1 | 0 | 0 | 1 | 0 | MXP-509 | 0.061 | 0.061 |  | Loop2 | Loop ok | 0.968 | 2000 | FP200 1.5mm | 0
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | NONE | 0 | 0 | 5100
Loop Driver Loop 3 | 0 | 1 | 0 | 0 | 1 | 0 |  |  |  | 5200 | Loop 3 | Loop ok | 0.968 | 2000 | FP200 1.5mm | 0
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | MXP-507 | 0 | 0.03 | 5400
Loop Driver Loop 4 | 0 | 0 | 0 | 0 | 1 | 0 | MXP-532 | 0.031 | 0.043 |  | Loop 4 | Loop ok | 0.968 | 2000 | FP200 1.5mm | 0
NO NETWORK Card | 0 | 1 | 0 | 0 | 1 | 0 | NONE | 0 | 0
NO PLUG-IN Card | 0 | 1 | 0 | 0 | 1 | 0
NO LED INDICATOR Card | 0 | 0 | 0 | 0 | 0 | 0
NO PRINTER | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 0.008 | 0.03
NO FAT INTERFACE | 0 | 1 | 0 | 0 | 1 | 0 | 100 | 0.016 | 0.06
| 0 | 1 | 0 | 0 | 1 | 0 | 150 | 0.024 | 0.09
ANCILLARY SUPPLY OUTPUT (AUX) | 0 | 1 | 0 | 0 | 1 | 0 | 200 | 0.032 | 0.12
[7 empty] | 250 | 0.04 | 0.15 |  | Nittan Evolution Battery and loop Calculation Spreadsheet Tool
Sounder Output A |  |  |  | 0 | 1 | 0 | NONE | 0 | 0
Sounder Output B |  |  |  | 0 | 1 | 0 |  |  |  |  | Instructions For Evolution 1 and EVO + Control Panels
|  |  |  | 0 | 1 | 0 | MXP-512 | 0.012 | 0.27
|  |  |  | 0 | 1 | 0 | NONE | 0 | 0 |  | Note:-Not Suitable For MX4000 (MXPro 4) Panels.Use the older Loop calculator program
Total | ΣQuiescent Load |  | 0.114 | ΣAlarm Load |  | 0.217
Standby Duration (hours) = | 24 | Hr | 2.736 |  | X(2 x 0.5) = | 0.217 | MXP-504 | 0.025 | 0.034 |  | For Evolution + panels Select panel size, For Evolution 1 use lower calculation panel.
|  |  |  | → (carry forward) + |  | 2.736 | MXP-504/508 | 0.025 | 0.099
[5 empty] | Total Load (Quiescent + Alarm) = | 2.953 | NONE | 0 | 0 |  | Enter Loop Device quantities into the LOOP page tables
[5 empty] | X 1.25 (Battery De-rating factor)** = | 3.6912
OPTIONS: | [6 empty] | SND 85dB | 0.0003 | 0.0035 |  | Set Quantity of device LEDs active in alarm. In Evolution + panels the quantity can be set
LCD DIMMING MODE | OFF | [5 empty] | SND 90dB | 0.0003 | 0.00825 |  | in the configuration, For Evolution 1 the quantity is fixed at 8 per loop.
NETWORK | NONE | [9 empty] | The User must set the LED quantity in the Table. This is important as it can have significant
ROUTING / RELAY CARDS | NONE | [9 empty] | impact on the loop calculation.
LED CARDS - NBR OF LEDS | NONE
PRINTER | NONE | [9 empty] | In the Loop Table select the type of cable to be used in the Installation.
FAT/FBF/FSD/ÜE INTERFACE | NONE | [9 empty] | Enter an estimate of the Installed loop cable length.
MINIMUM ENCLOSURE | SMALL | [9 empty] | Maximum suggested loop load is 80% of 500mA
The Volt Drop calculation is made as worst case scenario with the full
PANEL |  | Quiescent Load |  |  | Fire Alarm Load | [5 empty] | load being applied to the end of the cable length.
evolution 1 | I(A) | X | Total | I(A) | X | Total
Display & Loop Driver Card | 0.138 | 1 | 0.138 | 0.155 | 1 | 0.155 |  |  |  |  | The loop Quiescent and alarm loads will be automatically entered into the Battery Standby
Sensor / Loop Current* | 0 | 1.5 | 0 | 0.04 | 1.5 | 0.06 |  |  |  |  | Calculator. Additional loadings must be added into the battery Calculation tables such as
Conventional sounder loads and accessories . Check that the Standby Time has been set to
ANCILLARY SUPPLY OUTPUT (AUX) | 0 | 1 | 0 | 0 | 1 | 0 |  |  |  |  | the specified timescale for the installation.
Sounder Output A |  |  |  | 0 | 1 | 0
Sounder Output B |  |  |  | 0 | 1 | 0
|  |  |  | 0 | 1
|  |  |  | 0 | 1
Total | ΣQuiescent Load |  | 0.138 | ΣAlarm Load |  | 0.215
Standby Duration (hours) = | 24 | Hr | 3.312 |  | X(2 x 0.5) = | 0.215
|  |  |  | → (carry forward) + |  | 3.312
[5 empty] | Total Load (Quiescent + Alarm) = | 3.527
[5 empty] | X 1.25 (Battery De-rating factor)** = | 4.4088

## Loop 1
Loop Power Current consumption checker | Evolution 1 has 8 leds active in alarm, Evo + panel can have up to 10 leds active (set by Config)
EVO+ & Evolution 1 Panels only | [5 empty] | Evolution +
Nittan Model Name | Qty | Standby (A) | Standby Sum (A) | Alarm (A) | Alarm Sum (A) | CPU Points | Points Sum | Remark
Maximum No of leds Active in alarm (Determined by Panel spec) | 8 | 0 | 0 | 0.005 | 0.04 | 0
EV-P Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-DP Dual Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-A1R RATE OF RISE HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-CS HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-PH combination optical smoke and heat detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-A2R Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-CS Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-PS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
EV-PYS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
UB-6-EV Standard base for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
STB-4SE-EV DEEP BASE for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
EV-B-SCI -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-DIN-SCI DIN Rail -ve Isolator |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-SPB-SCI Waterproof -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-MCP RESET Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP RESET Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP24 Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP67 Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP24 Manual Call Point with -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP67 Waterproof Manual Call Point -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-SDR Base Sounder with integral Base |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-SDR Sounder |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-HIOP-SB-SCI High Output Sounder Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN-SCI High Output Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR-SCI High Output Sounder with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SB High Output Sounder Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN High Output Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR High Output Sounder |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-AV2 Sounder/Beacon (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-PSBCN Beacon Base (for EV-PS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-PYSBCN Beacon Base (for EV-PYS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-24VRL Addressable Relay Base |  | 0.0001 | 0 | 0.0002 | 0 | 0 | 0
EV-OP Output Module |  | 0.00046 | 0 | 0.0045 | 0 | 1 | 0
EV-IP Input Module |  | 0.000505 | 0 | 0.0005 | 0 | 2 | 0
EV-SIO Single Input/Output module |  | 0.0003 | 0 | 0.003 | 0 | 2 | 0
EV-SCM Sounder Control Module |  | 0.00075 | 0 | 0.0045 | 0 | 1 | 0
EV-ZMU Zone Monitor Module |  | 0.00028 | 0 | 0.0003 | 0 | 2 | 0
EV-SBM Sounder Booster Module |  | 0 | 0 |  | 0 | 0 | 0
EV-MINI I/P Mini Input Module |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-OP2 Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 1 | 0
EV-IP2 Dual Input module |  | 0.00072 | 0 | 0.0055 | 0 | 2 | 0
EV-2I1O Dual Input/Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 3 | 0
EV-3IO Triple Input/Output module |  | 0.00086 | 0 | 0.0083 | 0 | 6 | 0
EV-IO-420 4-20mA Input/Relay Output module |  | 0.00063 | 0 | 0.0078 | 0 | 3 | 0
EV-SCM2 Dual Output Sounder Control Module |  | 0.00074 | 0 | 0.0031 | 0 | 2 | 0
EV-ZMU2 Dual Input Zone Monitor Module |  | 0.015 | 0 | 0.0035 | 0 | 2 | 0
EV-Mini IP2 Miniature Input module |  | 0.00069 | 0 | 0.0033 | 0 | 1 | 0
EV-LASD1 Aspirating Detector |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-LASD2 Aspirating Detector |  | 0.00092 | 0 | 0.00092 | 0 | 2 | 0
EV-Firebeam Detector |  | 0.004 | 0 | 0.004 | 0 | 1 | 0
STA-R1 Remote Indicator |  | 0 | 0 | 0.002 | 0 | 0 | 0
Total Quantity of Addressable devices per loop | 0 | Standby Sum | 0 | Alarm Sum | 0.04 | Points Sum | 0
Load ok
Select Cable type |  | Ohms/KM
FP200 1.5mm |  | 12.1
Enter Total loop Cable length in Metres
1000
Loop Voltage Drop in Alarm
0.968 |  | Loop ok
Calculated Maximum cable length in Metres
2000

## Loop 2
Loop Power Current consumption checker | Evolution 1 has 8 leds active in alarm, Evo + panel can have up to 10 leds active (set by Config)
EVO+ & Evolution 1 Panels only | [5 empty] | Evolution +
Nittan Model Name | Qty | Standby (A) | Standby Sum (A) | Alarm (A) | Alarm Sum (A) | CPU Points | Points Sum | Remark
Maximum No of leds Active in alarm (Determined by Panel spec) | 8 | 0 | 0 | 0.005 | 0.04 | 0
EV-P Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-DP Dual Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-A1R RATE OF RISE HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-CS HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-PH combination optical smoke and heat detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-A2R Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-CS Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-PS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
EV-PYS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
UB-6-EV Standard base for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
STB-4SE-EV DEEP BASE for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
EV-B-SCI -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-DIN-SCI DIN Rail -ve Isolator |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-SPB-SCI Waterproof -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-MCP RESET Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP RESET Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP24 Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP67 Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP24 Manual Call Point with -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP67 Waterproof Manual Call Point -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-SDR Base Sounder with integral Base |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-SDR Sounder |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-HIOP-SB-SCI High Output Sounder Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN-SCI High Output Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR-SCI High Output Sounder with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SB High Output Sounder Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN High Output Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR High Output Sounder |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-AV2 Sounder/Beacon (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-PSBCN Beacon Base (for EV-PS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-PYSBCN Beacon Base (for EV-PYS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-24VRL Addressable Relay Base |  | 0.0001 | 0 | 0.0002 | 0 | 0 | 0
EV-OP Output Module |  | 0.00046 | 0 | 0.0045 | 0 | 1 | 0
EV-IP Input Module |  | 0.000505 | 0 | 0.0005 | 0 | 2 | 0
EV-SIO Single Input/Output module |  | 0.0003 | 0 | 0.003 | 0 | 2 | 0
EV-SCM Sounder Control Module |  | 0.00075 | 0 | 0.0045 | 0 | 1 | 0
EV-ZMU Zone Monitor Module |  | 0.00028 | 0 | 0.0003 | 0 | 2 | 0
EV-SBM Sounder Booster Module |  | 0 | 0 |  | 0 | 0 | 0
EV-MINI I/P Mini Input Module |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-OP2 Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 1 | 0
EV-IP2 Dual Input module |  | 0.00072 | 0 | 0.0055 | 0 | 2 | 0
EV-2I1O Dual Input/Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 3 | 0
EV-3IO Triple Input/Output module |  | 0.00086 | 0 | 0.0083 | 0 | 6 | 0
EV-IO-420 4-20mA Input/Relay Output module |  | 0.00063 | 0 | 0.0078 | 0 | 3 | 0
EV-SCM2 Dual Output Sounder Control Module |  | 0.00074 | 0 | 0.0031 | 0 | 2 | 0
EV-ZMU2 Dual Input Zone Monitor Module |  | 0.015 | 0 | 0.0035 | 0 | 2 | 0
EV-Mini IP2 Miniature Input module |  | 0.00069 | 0 | 0.0033 | 0 | 1 | 0
EV-LASD1 Aspirating Detector |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-LASD2 Aspirating Detector |  | 0.00092 | 0 | 0.00092 | 0 | 2 | 0
EV-Firebeam Detector |  | 0.004 | 0 | 0.004 | 0 | 1 | 0
STA-R1 Remote Indicator |  | 0 | 0 | 0.002 | 0 | 0 | 0
Total Quantity of Addressable devices per loop | 0 | Standby Sum | 0 | Alarm Sum | 0.04 | Points Sum | 0
Load ok
Select Cable type |  | Ohms/KM
FP200 1.5mm |  | 12.1
Enter Total loop Cable length in Metres
1000
Loop Voltage Drop in Alarm
0.968 |  | Loop ok
Calculated Maximum cable length in Metres
2000

## Loop 3
Loop Power Current consumption checker | Evolution 1 has 8 leds active in alarm, Evo + panel can have up to 10 leds active (set by Config)
EVO+ & Evolution 1 Panels only | [5 empty] | Evolution +
Nittan Model Name | Qty | Standby (A) | Standby Sum (A) | Alarm (A) | Alarm Sum (A) | CPU Points | Points Sum | Remark
Maximum No of leds Active in alarm (Determined by Panel spec) | 8 | 0 | 0 | 0.005 | 0.04 | 0
EV-P Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-DP Dual Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-A1R RATE OF RISE HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-CS HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-PH combination optical smoke and heat detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-A2R Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-CS Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-PS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
EV-PYS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
UB-6-EV Standard base for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
STB-4SE-EV DEEP BASE for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
EV-B-SCI -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-DIN-SCI DIN Rail -ve Isolator |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-SPB-SCI Waterproof -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-MCP RESET Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP RESET Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP24 Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP67 Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP24 Manual Call Point with -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP67 Waterproof Manual Call Point -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-SDR Base Sounder with integral Base |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-SDR Sounder |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-HIOP-SB-SCI High Output Sounder Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN-SCI High Output Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR-SCI High Output Sounder with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SB High Output Sounder Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN High Output Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR High Output Sounder |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-AV2 Sounder/Beacon (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-PSBCN Beacon Base (for EV-PS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-PYSBCN Beacon Base (for EV-PYS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-24VRL Addressable Relay Base |  | 0.0001 | 0 | 0.0002 | 0 | 0 | 0
EV-OP Output Module |  | 0.00046 | 0 | 0.0045 | 0 | 1 | 0
EV-IP Input Module |  | 0.000505 | 0 | 0.0005 | 0 | 2 | 0
EV-SIO Single Input/Output module |  | 0.0003 | 0 | 0.003 | 0 | 2 | 0
EV-SCM Sounder Control Module |  | 0.00075 | 0 | 0.0045 | 0 | 1 | 0
EV-ZMU Zone Monitor Module |  | 0.00028 | 0 | 0.0003 | 0 | 2 | 0
EV-SBM Sounder Booster Module |  | 0 | 0 |  | 0 | 0 | 0
EV-MINI I/P Mini Input Module |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-OP2 Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 1 | 0
EV-IP2 Dual Input module |  | 0.00072 | 0 | 0.0055 | 0 | 2 | 0
EV-2I1O Dual Input/Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 3 | 0
EV-3IO Triple Input/Output module |  | 0.00086 | 0 | 0.0083 | 0 | 6 | 0
EV-IO-420 4-20mA Input/Relay Output module |  | 0.00063 | 0 | 0.0078 | 0 | 3 | 0
EV-SCM2 Dual Output Sounder Control Module |  | 0.00074 | 0 | 0.0031 | 0 | 2 | 0
EV-ZMU2 Dual Input Zone Monitor Module |  | 0.015 | 0 | 0.0035 | 0 | 2 | 0
EV-Mini IP2 Miniature Input module |  | 0.00069 | 0 | 0.0033 | 0 | 1 | 0
EV-LASD1 Aspirating Detector |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-LASD2 Aspirating Detector |  | 0.00092 | 0 | 0.00092 | 0 | 2 | 0
EV-Firebeam Detector |  | 0.004 | 0 | 0.004 | 0 | 1 | 0
STA-R1 Remote Indicator |  | 0 | 0 | 0.002 | 0 | 0 | 0
Total Quantity of Addressable devices per loop | 0 | Standby Sum | 0 | Alarm Sum | 0.04 | Points Sum | 0
Load ok
Select Cable type |  | Ohms/KM
FP200 1.5mm |  | 12.1
Enter Total loop Cable length in Metres
1000
Loop Voltage Drop in Alarm
0.968 |  | Loop ok
Calculated Maximum cable length in Metres
2000

## Loop 4
Loop Power Current consumption checker | Evolution 1 has 8 leds active in alarm, Evo + panel can have up to 10 leds active (set by Config)
EVO+ & Evolution 1 Panels only | [5 empty] | Evolution +
Nittan Model Name | Qty | Standby (A) | Standby Sum (A) | Alarm (A) | Alarm Sum (A) | CPU Points | Points Sum | Remark
Maximum No of leds Active in alarm (Determined by Panel spec) | 8 | 0 | 0 | 0.005 | 0.04 | 0
EV-P Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-DP Dual Optical smoke detector |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-A1R RATE OF RISE HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-H-CS HEAT DETECTOR |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-PH combination optical smoke and heat detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-A2R Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-DPH-CS Dual Optical/Heat Detector |  | 0.0002 | 0 | 0.0002 | 0 | 2 | 0
EV-PS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
EV-PYS Optical Detector with In-built Sounder |  | 0.0002 | 0 | 0.0035 | 0 | 2 | 0
UB-6-EV Standard base for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
STB-4SE-EV DEEP BASE for use with Evolution detectors |  | 0 | 0 | 0 | 0 | 0 | 0
EV-B-SCI -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-DIN-SCI DIN Rail -ve Isolator |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-SPB-SCI Waterproof -ve Isolator Base |  | 6e-05 | 0 | 6e-05 | 0 | 0 | 0
EV-MCP RESET Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP RESET Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP24 Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-IP67 Waterproof Manual Call Point |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP24 Manual Call Point with -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-MCP2-SCI-IP67 Waterproof Manual Call Point -ve Isolator |  | 0.0002 | 0 | 0.0002 | 0 | 1 | 0
EV-SDR Base Sounder with integral Base |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-SDR Sounder |  | 0.0002 | 0 | 0.0068 | 0 | 1 | 0
EV-HIOP-SB-SCI High Output Sounder Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN-SCI High Output Beacon with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR-SCI High Output Sounder with -ve Isolator |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SB High Output Sounder Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-BCN High Output Beacon |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-HIOP-SDR High Output Sounder |  | 0.0002 | 0 | 0.02 | 0 | 1 | 0
EV-AV2 Sounder/Beacon (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (low volume) |  | 0.0002 | 0 | 0.0095 | 0 | 2 | 0
EV-AV2 Sounder/Beacon Base (High volume) Default setting |  | 0.0002 | 0 | 0.014 | 0 | 2 | 0
EV-PSBCN Beacon Base (for EV-PS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-PYSBCN Beacon Base (for EV-PYS) |  | 0 | 0 | 0.0062 | 0 | 0 | 0
EV-24VRL Addressable Relay Base |  | 0.0001 | 0 | 0.0002 | 0 | 0 | 0
EV-OP Output Module |  | 0.00046 | 0 | 0.0045 | 0 | 1 | 0
EV-IP Input Module |  | 0.000505 | 0 | 0.0005 | 0 | 2 | 0
EV-SIO Single Input/Output module |  | 0.0003 | 0 | 0.003 | 0 | 2 | 0
EV-SCM Sounder Control Module |  | 0.00075 | 0 | 0.0045 | 0 | 1 | 0
EV-ZMU Zone Monitor Module |  | 0.00028 | 0 | 0.0003 | 0 | 2 | 0
EV-SBM Sounder Booster Module |  | 0 | 0 |  | 0 | 0 | 0
EV-MINI I/P Mini Input Module |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-OP2 Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 1 | 0
EV-IP2 Dual Input module |  | 0.00072 | 0 | 0.0055 | 0 | 2 | 0
EV-2I1O Dual Input/Single Output module |  | 0.00072 | 0 | 0.0055 | 0 | 3 | 0
EV-3IO Triple Input/Output module |  | 0.00086 | 0 | 0.0083 | 0 | 6 | 0
EV-IO-420 4-20mA Input/Relay Output module |  | 0.00063 | 0 | 0.0078 | 0 | 3 | 0
EV-SCM2 Dual Output Sounder Control Module |  | 0.00074 | 0 | 0.0031 | 0 | 2 | 0
EV-ZMU2 Dual Input Zone Monitor Module |  | 0.015 | 0 | 0.0035 | 0 | 2 | 0
EV-Mini IP2 Miniature Input module |  | 0.00069 | 0 | 0.0033 | 0 | 1 | 0
EV-LASD1 Aspirating Detector |  | 0.00046 | 0 | 0.00046 | 0 | 1 | 0
EV-LASD2 Aspirating Detector |  | 0.00092 | 0 | 0.00092 | 0 | 2 | 0
EV-Firebeam Detector |  | 0.004 | 0 | 0.004 | 0 | 1 | 0
STA-R1 Remote Indicator |  | 0 | 0 | 0.002 | 0 | 0 | 0
Total Quantity of Addressable devices per loop | 0 | Standby Sum | 0 | Alarm Sum | 0.04 | Points Sum | 0
Load ok
Select Cable type |  | Ohms/KM
FP200 1.5mm |  | 12.1
Enter Total loop Cable length in Metres
1000
Loop Voltage Drop in Alarm
0.968 |  | Loop ok
Calculated Maximum cable length in Metres
2000

## Sheet2 (hidden)
Cable Parameters
| Ohms per KM | mH per km | uF per km
Cable manufacturer | Resistance (per Core) | Inductance (per Core) | Capacitance (Core to Core)
Fire Tuff (2 Core) 1.0mm | 19 | 0.475 | 0.175
Fire Tuff (2 Core ) 1.5mm | 12.5 | 0.5 | 0.205
Fire Tuff (2 Core ) 2.5mm | 7.5 | 0.375 | 0.24
Fire Tuff (3/4 core) 1.0mm | 16.1 | 0.403 | 0.175
Fire Tuff (3/4 core) 1.5mm | 12.1 | 0.484 | 0.205
Fire Tuff (3/4 core) 2.5mm | 7.4 | 0.371 | 0.24
FP200 1.0mm | 16.1 | 0.72 | 0.15
FP200 1.5mm | 12.1 | 0.68 | 0.17
FP200 2.5mm | 7.4 | 0.62 | 0.21
MICC 1.0mm | 17.2 | 0.56 | 0.18
MICC 1.5mm | 11.5 | 0.534 | 0.19
MICC 2.5mm | 6.9 | 0.52 | 0.22
SWA (2 core) | 8.8 | 0.68 | 0.15
Ventcroft No Burn Standard 1.5mm | 12.1 | 0.297 | 0.13
Ventcrogt No Burn Standard 2.5mm | 7.41 | 0.26 | 0.145
Ventcroft No Burn enhanced 1.5mm | 12.1 | 0.38 | 0.125
Ventcroft No Burn enhanced 2.5mm | 7.41 | 0.28 | 0.155